| PROTOCOL FOR THE WAREHOUSE (COOL ROOM) MAPPING |  |
| --- | --- |
| # COMPANY NAME | # Pharm Trade- |
| # ASSET NAME | # Warehouse cool room-:15 to 25°C- |
| # LOCATION | # DIP, Dubai, United Arab Emirates |

| PROTOCOL PREPARED BY |  |  |
| --- | --- | --- |
| NAME & DESIGNATION | SIGNATURE | DATE |
| Site Engineer Westcal Instrumentation and Calibration Services LLC, Dubai |  | ## 25-09-2026 |

| PROTOCOL APPROVED & REVIEW BY |  |  |
| --- | --- | --- |
| NAME & DESIGNATION | SIGNATURE | DATE |
| Name: Ali 0501234567 Title: Contact Company: Pharm Trade |  |  |
| Name: Raifan Title: Sales Company: Pharm Trade |  |  |
| Name: Office Title: Coordinator Company: Pharm Trade |  |  |

| CHANGE HISTORY |  |  |  |  |
| --- | --- | --- | --- | --- |
| NAME | REASON FOR CHANGE | REVISION | ISSUED DATE |
|  | New document | 0 | ## 25-09-2026 |
| Office | Results Added | 0 |  |

SCOPE OF THIS PROTOCOL:

| Study type | Temperature and Humidity Mapping study |
| --- | --- |
| Client Name | Pharm Trade |
| Asset Type | Warehouse cool room |
| Description and Location | DIP, Dubai, United Arab Emirates |
| Temperature range to be mapped | Low limit 15°C High limit 25°C |
| Humidity range to be mapped | Maximum by |
| Duration of testing | 3 |
| Date of Testing | 26-09-2026 to 28-09-2026 |

Reference Standards: This mapping study is carried out as per WHO Technical Report Series, No. 961, 2011.

TABLE of CONTENTS

1	IDENTIFICATION OF THE QUALIFICATION TEAM	6

2	DEFINITIONS AND ACRONYMS	7

3	SCOPE OF THE WORK	8

4	OBJECTIVE	8

5	RATIONALE	9

6	APPLICABILITY	10

7        RESPONSIBILITY	10

8        DOCUMENTATION	11

8.1 	MANUAL ENTRIES IN PROTOCOL	11

8.2	DATA SHEETS	11

9       TEMPERATURE & HUMIDITY DISTRIBUTION VERIFICATION REPORT	11

10     WAREHOUSE (COOL ROOM)  DESCRIPTION	12

11     KEY OPERATING PARAMETERS	13

12     TEMPERATURE & HUMIDITY DISTRIBUTION VERIFICATION- Winter Season 2026	14

13      ANALYSIS		16

# IDENTIFICATION OF THE QUALIFICATION TEAM

To identify the individuals involved in the execution of this qualification, their names, titles, and corresponding specimen signatures and initials are provided below.

| Name | Title | Signature | Initial |
| --- | --- | --- | --- |
|  | Engineer |  |  |

# 2	DEFINITIONS AND ACRONYMS

To aid in the understanding of the terms and acronyms used in this document, brief technical definitions are provided below.

| Terms | Definitions |
| --- | --- |
| Change Parts | Parts to fit different size / format or application. |
| Deviation | Any discrepancy between the protocol and the actual performed test, test function methodology etc. |
| Instrument | A device that interprets a mechanical, digital or analog signal generated by a sensor, and converts it into engineering units (°C, % RH, mA, etc.) through scaling. |
| Key Operating Parameters | Parameters that must be maintained to process or produce products with consistent quality attributes and those that may have an impact on the proper operation of the equipment. |
| Main Equipment | Major equipment to be qualified. |
| D | Deviation |
| ID | Identification |
| N/Ap. | Not Applicable |
| N/Av. | Not Available |
| N/Sp. | Not Specified |
| NIST | National Institute of Standards and Technology |
| CFR | Code of Federal Regulations |
| PQ | Performance Qualification |
| PM | Preventive Maintenance |
| QA | Quality Assurance |
| QC | Quality Control |
| S/N | Serial number |

# SCOPE OF THE WORK

The Temperature & Humidity Distribution Verification Protocol is a comprehensive document intended to guide the personnel responsible for verifying the temperature and humidity distribution within the Warehouse cool room during 2026.

# OBJECTIVE

- Conduct a temperature mapping study to evaluate the distribution of temperature throughout the Warehouse.

- Conduct a humidity mapping study to evaluate the distribution of humidity within the Warehouse.

- Provide a description of the equipment used, including its major components and their functions.

- Ensure that proper identification and documentation practices are in place.

- Verify that the physical characteristics of the Warehouse are compatible with the intended equipment utilization.

- Confirm that appropriate operational procedures and training programs are established.

- Identify the hot and cold points within the Warehouse.

- Recommended suitable locations for continuous monitoring sensors, based on identified hot and cold points.

- Perform the mapping study during two seasonal conditions (summer and winter). Recommendations from the first climatic study will be reviewed and updated the following the second study. Results from the summer study will be treated as the worst-case scenario, forming the basis for final recommendations.

- Determine the required number of data loggers based on the Warehouse (Cool Room) volume and in accordance with applicable WHO standards.

# RATIONALE

The study of the temperature & humidity distribution inside the Warehouse cool roomis the establishment of documented evidence of the temperature & humidity distribution during 2026 .

The protocol is designed to allow analysis of temperature & humidity distribution inside the Warehouse cool room  .  Temperature & humidity distribution will be analyzed as follows:

- Warehouse cool room temperature & humidity distribution verification  -  2026

- The temperature & humidity distribution during summer will be verified by conducting a minimum of 3temperature & humidity mapping of the Warehouse cool roomusing 12  IMINI Data Loggers. These data loggers will be positioned as described in this protocol (one (1) of these data loggers will be located outside of the Warehouse cool room(1)).  Data logger’s location was established to represent product locations; including hottest and coldest location (high racking and near AC units, low racking and near entrance doors).  The reading interval will be set at 3 minutes for the mapping.  During the mapping the Warehouse cool roomwill be loaded between 75% and 90% of its capacity. The temperature & humidity set point of all temperature & humidity controllers will be documented.

The temperature & humidity distribution verification must be conducted by trained and experienced technical personnel and must be documented in a scientific manner using this established format.

The study is meant to be representative and to be close to the real use of the Warehouse cool room. The temperature & humidity distribution study is to be executed during normal working condition

IMINI Temperature & humidity Data Loggers will be used to measure and record temperature & humidity.  Each data logger has been calibrated and calibration certificates included in the reports will be placed in the Supporting Documents section.  These instruments will not be post-calibrated following the execution of this temperature & humidity distribution verification.

Escort Console Plus software will be used to program data loggers, to download data and to generate reports which are compliant to PIC/S GMP Annex 11 and 21 CFR Part 11 requirements.

The temperature & humidity distribution verification documented in this protocol only covers Warehouse cool room of Pharm trade located in DIP, Dubai, United Arab Emirates.

# APPLICABILITY

### All Westcal Instrumentation and Calibration Services LLC personnel involved in the Temperature & Humidity Distribution Verification shall adhere to the procedures outlined in this protocol.

### 7	RESPONSIBILITY

This Warehouse cool room temperature & humidity distribution verification protocol must be respected by all Vacker LLC and Pharmatrade employees during processing.

The responsibility of the Warehouse cool room temperature & humidity distribution verification is attributed to the following:

Responsibility for the implementation of the Temperature & Humidity Distribution Verification is assigned as follows:

| Responsibilities |  |  |
| --- | --- | --- |
| Task | Westcal Instrumentation and Calibration Services LLC | Pharm Trade |
| Make available all technical documentation required for the mapping of the Warehouse. |  |  |
| Collect information. |  |  |
| Write the protocol. |  |  |
| Review and approve the protocol. |  |  |
| Coordinate activity. |  |  |
| Arrange loading and unloading goods for the test |  |  |
| Execute the test described in the protocol. |  |  |
| Compile and analyze data. |  |  |
| Issue the final report. |  |  |
| Review and approve the final report. |  |  |

### DOCUMENTATION

## 8.1 	MANUAL ENTRIES IN PROTOCOL

All manual entries will be written in indelible ink.

Any error must be crossed out with a single line stroke, and the correct information must be entered below or above the error.

All corrections must be initialled and dated.

## 8.2	DATA SHEETS

Information will be directly recorded in the Section «Test Data Sheet» of this protocol.  Here is a brief description of each section:

| Section | Description |
| --- | --- |
| Data | Schema, tables, raw data, summary tables. |
| Comments | Discussion of any unusual observations during the test or significant test conditions not defined in the test procedure. |
| Tested by | Signature and corresponding date for the person performing the test. |
| Verified by | Signature and corresponding date for the person verifying the test data. |

### TEMPERATURE & HUMIDITY DISTRIBUTION VERIFICATION REPORT

The Temperature & Humidity distribution verification report will be written following the execution of the protocol and will include the sections listed below.

| Section | Description |
| --- | --- |
| Objective | Description of the objectives of the Warehouse cool room temperature & humidity distribution verification. |
| Summary | Summary and discussion of the results of the execution of this protocol. |
| Conclusion | General conclusion of the temperature & humidity distribution verification inside the Warehouse cool room . |

### WAREHOUSE (COOL ROOM) DESCRIPTION

The Warehouse cool roomof Pharm Trade is located at DIP, Dubai, United Arab Emirates .

The total surface area of the Warehouse cool roomis about 20m x 10m . The Warehouse cool roomis designed to store pharmaceuticals products.

The air circulation inside the Warehouse cool roomis ensured by the air conditioning system which are controlled by one (01) temperature controller.

The Warehouse cool roomis designed to keep the products at a temperature between 15 to 25°C and maximum humidity of  .

### KEY OPERATING PARAMETERS

List all parameters that must be maintained to process or produce products with consistent quality attributes and those that may have an impact on the proper operation of the Warehouse cool room   .

| Parameter | Set point | Range |
| --- | --- | --- |
| Temperature | 20°C | 15 to 25°C |
| Humidity | Nil | Max |

### TEMPERATURE & HUMIDITY DISTRIBUTION VERIFICATION- Winter Season 2026

Objective

To verify the temperature & humidity distribution of the Warehouse cool room during 2026.

Acceptance Criteria

- Each of the 12 IMINI Data Loggers located inside the Warehouse cool room should maintain the temperature between 15 to 25°C. - Each of the 12 IMINI Data Loggers located inside the Warehouse cool room should maintain the humidity within . - Any regular pattern of regular Highs or Lows for any of Data loggers or any particular area to be analyzed. - At least {minimum_number of loggers_ to be mapped}} of the 12 IMINI Data Loggers is installed inside the Warehouse cool room must remain functional during and after the test. - No criterion is required for IMINI data loggers installed outside the warehouse-3. The data collected by this IMINI data logger are for information purpose only.

| Prerequisite |  |  |
| --- | --- | --- |
| ID Number | Instrument Name | Function |
| software | Console Plus software | To display and record the temperature & humidity measured by the IMINI Data Loggers. |
| DL-001 to 12 and DL-OUTSIDE | IMINI Data Loggers | To measure and record the temperature & humidity. |

Methodology

- Program the IMINI Data Loggers to record the temperature & humidity with a 3 minutes sampling rate. - Install the IMINI Data Loggers as described in Schema – IMINI Data Loggers Location (Refer to Attachment 1, Test Data Sheet). - Install the IMINI Data Logger DL-OUT outside the Warehouse cool roomto record the ambient air temperature & humidity (1). - Record in the Test Data Sheet, the temperature & humidity distribution verification start time / date and continue recording the temperature & humidity for at least 3. Note: Temperature & Humidity distribution verification start time corresponds to either 30 minutes after the logger’s installation is completed or to the logger’s programmed start time, if happening later. Only data recorded after established start time will be considered for data compilation. - Record all temperature & humidity controller set point in the temperature & humidity Controller Information table in Test Data Sheet. - At the end of the temperature & humidity distribution verification period, download all IMINI Data Loggers; generate raw data printouts and place them in Attachment 1. - Generate the Excel (or equivalent) spreadsheets and graphs. Sign off all the pages.

(1)Outside of the building.

Test Data

- Complete Test Data Sheet. - Enclose all test data in Attachment 1 Test Data Sheet. - Enclose TEMPNIX Data Loggers calibration reports in attachment 2.

### ANALYSIS

  - Mean Kinetic Temperature

- Mean kinetic temperature (MKT) is a simplified way of expressing the overall effect of temperature fluctuations. Mean Kinetic Temperature (MKT) is defined as the single calculated temperature at which the total amount of degradation over a particular period is equal to the sum of the individual degradations that would occur at various temperature.

- A single derived temperature that, if maintained over a defined period of time, affords the same thermal challenge to a drug substance or drug product as would be experienced over a range of both higher and lower temperature for an equivalent defined period. 
The mean kinetic temperature can be expressed as:

- Where:

- is the mean kinetic temperature in kelvins

- is the activation energy (typically within 60–100 kJ·mol-1 for solids or liquids)

- is the gas constant

- to  are the temperature at each of the sample points in kelvins

- to  are time intervals at each of the sample points

- When the temperature readings are taken at the same interval (i.e.,  =  =  = ), the above equation is reduced to:

- Where:

- is the number of temperature sample points

- Note: In this study MKT is not considered as an acceptance criteria. The acceptance criteria is specified that all data loggers should remain within the specified limits.

  - Hot and Cold Points

Hot and cold points are identified by analyzing the individual value of all data loggers

TEST DATA SHEET

DATA LOGGERS’ LOCATION

Warehouse cool room

One (1) data logger will be installed approximately every 8 meters (or less), arranged in three vertical rows—low (around 0.5 m), mid (2.5 m), and high (approximately 4.5 m)—for all full-height racking areas. For sections with a mezzanine floor, data loggers will also be distributed across three height levels. Detailed placement is illustrated in the accompanying drawings.

The indicated positions and heights are approximate and may be adjusted as necessary. Any deviations will be recorded in the "Comments" column of the respective installation tables.

Dl-Out to be placed outdoors to record ambient Temperature & Humidity throughout the duration of the study.

TEST DATA SHEET

TEMPNIX   DATA LOGGERS’ LOCATION (CONTINUED)

Warehouse cool room-

| Data Logger ID number | Height (1) (m) |  | Comments (Document any pertinent information in order to localize data loggers) |
| --- | --- | --- | --- |
| DL-001 | 0.5 |  | N/Ap. |
| DL-002 | 2.0 |  |  |
| DL-003 | 3.0 |  |  |
| DL-004 | 0.5 |  |  |
| DL-005 | 2.0 |  |  |
| DL-006 | 3.0 |  |  |
| DL-007 | 0.5 |  |  |
| DL-008 | 2.0 |  |  |
| DL-009 | 3.0 |  |  |
| DL-010 | 0.5 |  |  |
| DL-011 | 2.0 |  |  |
| DL-012 | 3.0 |  |  |
| DL-013 | 0.5 |  |  |
| DL-014 | 2.0 |  |  |
| DL-015 | 3.0 |  |  |
| DL-016 | 0.5 |  |  |
| DL-017 | 2.0 |  |  |
| DL-018 | 3.0 |  |  |
| DL-019 | 0.5 |  |  |
| DL-020 | 2.0 |  |  |
| DL-021 | 3.0 |  |  |
| DL-022 | 0.5 |  |  |
| DL-023 | 2.0 |  |  |
| DL-024 | 3.0 |  |  |
| DL-025 | 0.5 |  |  |
| Data Logger ID number |  | Height(1) (m) | Comments (Document any pertinent information in order to localize data loggers) |
| DL-026 |  | 2.0 |  |
| DL-027 |  | 3.0 |  |
| DL-028 |  | 0.5 |  |
| DL-029 |  | 2.0 |  |
| DL-030 |  | 3.0 |  |
| DL-031 |  | 0.5 |  |
| DL-032 |  | 2.0 |  |
| DL-033 |  | 3.0 |  |
| DL-034 |  | 0.5 |  |
| DL-035 |  | 2.0 |  |
| DL-036 |  | 3.0 |  |
| DL-037 |  | 0.5 |  |
| DL-038 |  | 2.0 |  |
| DL-039 |  | 3.0 |  |
| DL-040 |  | 0.5 |  |
| DL-041 |  | 2.0 |  |
| DL-042 |  | 3.0 |  |
| DL-043 |  | 0.5 |  |
| DL-044 |  | 2.0 |  |
| DL-045 |  | 3.0 |  |
| DL-046 |  | 0.5 |  |
| DL-047 |  | 2.0 |  |
| DL-048 |  | 3.0 |  |
| DL-049 |  | 0.5 |  |
| DL-050 |  | 2.0 |  |
| DL-051 |  | 3.0 |  |
| DL-052 |  | 0.5 |  |
| DL-053 |  | 2.0 |  |
| DL-054 |  | 3.0 |  |
| DL-OUT |  | N/Ap |  |

TEST DATA SHEET

TEMPERATURE DISTRIBUTION PERIOD

| Table of Results |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Tempnix Data Logger ID Number | Min. temp. recorded (°C) | Max temp. recorded (°C) | Mean Temp (°C) | Pass | Fail | Tested by | Date |
| DL-001 |  |  |  |  |  |  | 25-09-2026 |
| DL-002 |  |  |  |  |  |  |  |
| DL-003 |  |  |  |  |  |  |  |
| DL-004 |  |  |  |  |  |  |  |
| DL-005 |  |  |  |  |  |  |  |
| DL-006 |  |  |  |  |  |  |  |
| DL-007 |  |  |  |  |  |  |  |
| DL-008 |  |  |  |  |  |  |  |
| DL-009 |  |  |  |  |  |  |  |
| DL-010 |  |  |  |  |  |  |  |
| DL-011 |  |  |  |  |  |  |  |
| DL-012 |  |  |  |  |  |  |  |
| DL-013 |  |  |  |  |  |  |  |
| DL-014 |  |  |  |  |  |  |  |
| DL-015 |  |  |  |  |  |  |  |
| DL-016 |  |  |  |  |  |  |  |
| DL-017 |  |  |  |  |  |  |  |
| DL-018 |  |  |  |  |  |  |  |
| DL-019 |  |  |  |  |  |  |  |
| DL-020 |  |  |  |  |  |  |  |
| DL-021 |  |  |  |  |  |  |  |
| DL-022 |  |  |  |  |  |  |  |
| DL-023 |  |  |  |  |  |  |  |
| DL-024 |  |  |  |  |  |  |  |
| DL-025 |  |  |  |  |  |  |  |
| DL-026 |  |  |  |  |  |  |  |
| Table of Results |  |  |  |  |  |  |  |
| TEMPNIX Data Logger ID Number | Min. temp. recorded (°C) | Max temp. recorded (°C) | Mean Temp (°C) | Pass | Fail | Tested by | Date |
| DL-027 |  |  |  |  |  |  | 25-09-2026 |
| DL-028 |  |  |  |  |  |  |  |
| DL-029 |  |  |  |  |  |  |  |
| DL-030 |  |  |  |  |  |  |  |
| DL-031 |  |  |  |  |  |  |  |
| DL-032 |  |  |  |  |  |  |  |
| DL-033 |  |  |  |  |  |  |  |
| DL-034 |  |  |  |  |  |  |  |
| DL-035 |  |  |  |  |  |  |  |
| DL-036 |  |  |  |  |  |  |  |
| DL-037 |  |  |  |  |  |  |  |
| DL-038 |  |  |  |  |  |  |  |
| DL-039 |  |  |  |  |  |  |  |
| DL-040 |  |  |  |  |  |  |  |
| DL-041 |  |  |  |  |  |  |  |
| DL-042 |  |  |  |  |  |  |  |
| DL-043 |  |  |  |  |  |  |  |
| DL-044 |  |  |  |  |  |  |  |
| DL-045 |  |  |  |  |  |  |  |
| DL-046 |  |  |  |  |  |  |  |
| DL-047 |  |  |  |  |  |  |  |
| DL-048 |  |  |  |  |  |  |  |
| DL-049 |  |  |  |  |  |  |  |
| DL-050 |  |  |  |  |  |  |  |
| DL-051 |  |  |  |  |  |  |  |
| DL-052 |  |  |  |  |  |  |  |
| DL-053 |  |  |  |  |  |  |  |
| DL-054 |  |  |  |  |  |  |  |
| DL-OUT |  |  |  |  |  |  |  |

TEST DATA SHEET

HUMIDITY DISTRIBUTION PERIOD

| Tempnix Data Logger ID Number | Min. hum. recorded (%RH) | Max hum. recorded (%RH) | Pass | Fail | Tested by | Date |
| --- | --- | --- | --- | --- | --- | --- |
| DL-001 |  |  |  |  |  | 25-09-2026 |
| DL-002 |  |  |  |  |  |  |
| DL-003 |  |  |  |  |  |  |
| DL-004 |  |  |  |  |  |  |
| DL-005 |  |  |  |  |  |  |
| DL-006 |  |  |  |  |  |  |
| DL-007 |  |  |  |  |  |  |
| DL-008 |  |  |  |  |  |  |
| DL-009 |  |  |  |  |  |  |
| DL-010 |  |  |  |  |  |  |
| DL-011 |  |  |  |  |  |  |
| DL-012 |  |  |  |  |  |  |
| DL-013 |  |  |  |  |  |  |
| DL-014 |  |  |  |  |  |  |
| DL-015 |  |  |  |  |  |  |
| DL-016 |  |  |  |  |  |  |
| DL-017 |  |  |  |  |  |  |
| DL-018 |  |  |  |  |  |  |
| DL-019 |  |  |  |  |  |  |
| DL-020 |  |  |  |  |  |  |
| DL-021 |  |  |  |  |  |  |
| DL-022 |  |  |  |  |  |  |
| DL-023 |  |  |  |  |  |  |
| DL-024 |  |  |  |  |  |  |
| DL-025 |  |  |  |  |  |  |
| DL-026 |  |  |  |  |  |  |
| TEMPNIX Data Logger ID Number | Min. temp. recorded (°C) | Max temp. recorded (°C) | Pass | Fail | Tested by | Date |
| DL-027 |  |  |  |  |  | 25-09-2026 |
| DL-028 |  |  |  |  |  |  |
| DL-029 |  |  |  |  |  |  |
| DL-030 |  |  |  |  |  |  |
| DL-031 |  |  |  |  |  |  |
| DL-032 |  |  |  |  |  |  |
| DL-033 |  |  |  |  |  |  |
| DL-034 |  |  |  |  |  |  |
| DL-035 |  |  |  |  |  |  |
| DL-036 |  |  |  |  |  |  |
| DL-037 |  |  |  |  |  |  |
| DL-038 |  |  |  |  |  |  |
| DL-039 |  |  |  |  |  |  |
| DL-040 |  |  |  |  |  |  |
| DL-041 |  |  |  |  |  |  |
| DL-042 |  |  |  |  |  |  |
| DL-043 |  |  |  |  |  |  |
| DL-044 |  |  |  |  |  |  |
| DL-045 |  |  |  |  |  |  |
| DL-046 |  |  |  |  |  |  |
| DL-047 |  |  |  |  |  |  |
| DL-048 |  |  |  |  |  |  |
| DL-049 |  |  |  |  |  |  |
| DL-050 |  |  |  |  |  |  |
| DL-051 |  |  |  |  |  |  |
| DL-052 |  |  |  |  |  |  |
| DL-053 |  |  |  |  |  |  |
| DL-054 |  |  |  |  |  |  |
| DL-OUT |  |  |  |  |  |  |

TEST DATA SHEET

TEMPERATURE & HUMIDITY DISTRIBUTION PERIOD

|  | Date | Time (hh:mm) | Documented by | Date |
| --- | --- | --- | --- | --- |
| Temperature & Humidity distribution verification starts at: | 26-09-2026 | 09:30 | Office | 25-09-2026 |
| Temperature & Humidity distribution verification ends at: | 28-09-2026 | 09:30 |  |  |

TEST DATA SHEET

TEMPERATURE AND HUMIDITY DISTRIBUTION

SPREAD SHEETS AND GRAPHS

TEST DATA SHEET

DATA LOGGERS’ REPORTS

TEST DATA SHEET

CALIBRATION REPORTS OF DATA LOGGERS

TEST DATA SHEET

REVISION HISTORY

| Date | Change Summary | Reason for Change | Approved |
| --- | --- | --- | --- |